[image: image1.png]CleaverBrooks Qﬁ’



Model CFW

Commercial Boilers


Model CFW
SPECIFICATIONS

PART I. GENERAL
Hot Water Boilers – Near Condensing Boiler

1.01 
SCOPE

A. The  work  to  be  performed  consists  of  providing  all  labor, equipment,  materials, etc. to furnish  and  install  new  factory assembled, low-pressure hot water boilers as described in  the specifications herein.

B. Related Sections include the following:

1. Division 15 Section “Chemical Water Treatment” for feedwater treatment.

2. Division 15 Section “Breechings, Chimneys, and Stacks” for connections to chimneys, and stacks.

3. Division 15 Sections for control wiring for automatic temperature control.

1.02 
REFERENCES

A. Product Data:  Include rated capacities; shipping, installed,  and operating weights; furnished specialties; and accessories for each model indicated.

B. Shop
Drawings: Detail equipment assemblies and indicate dimensions, required clearances, and method of field assembly, components, and location and size of each field connection.
C. Wiring Diagrams: Detail wiring for power, signal, and control systems and differentiate between manufacturer-installed and field-installed wiring.

D. Source Quality Control Tests and Inspection Reports: Indicate and interpret test
results
for compliance
with performance requirements before shipping.

E. Field Test Reports: Indicate and interpret test results for compliance with performance requirements.

F. Maintenance Data: Include in the maintenance manuals specified in Division 1. Include parts list, maintenance guide, and wiring diagrams for each boiler.

G. Other:

1. 
ASME Section IV – Heating Boilers

2. 
ANSI Z21.13 – Gas Fired Low Pressure Boilers

3. 
NFPA 64/ANSI Z221.3 – National Fuel Code

4. 
FM – Factory Mutual

5. 
ASME CSD-1 – Controls and Safety Devices

6. 
XL-GAP (Formerly  GE-GAP / IRI)

7. 
UL or CSA Standards for Gas Fired Boilers

8. 
UBC – Uniform Building Code

9. 
UMC – Uniform Mechanical Code

10.  NEC – National Electrical Code

1.03. 
QUALITY ASSURANCE

A.
The equipment shall, as a minimum, be in strict compliance with the requirements of this specification and shall be the manufacturer's standard commercial product unless specified otherwise. Additional equipment features, details, accessories, appurtenances,  etc. which are   not  specifically  identified  but   which  are  a  part  of  the manufacturer's standard commercial product, shall be included in the equipment being furnished.

B.
The equipment shall be of the type, design, and size that the manufacturer currently offers for commercial sale and appears in the manufacturer's current catalogue. The equipment shall be new and fabricated from new materials and shall be free from defects in materials and workmanship

C. 
The equipment must fit within the allocated space, leaving ample allowance for maintenance and cleaning, and must leave suitable space for easy removal of all equipment appurtenances.

D.
All units of the same classification shall be identical to the extent necessary to ensure interchangeability of parts, assemblies, accessories, and spare parts wherever possible.

E.
To accept unit responsibility for the specified capacities, efficiencies, and performance, the boiler manufacturer shall certify in writing that the equipment being submitted shall perform as specified. The boiler manufacturer shall be responsible for guarantying that  the boiler provides the performance as specified herein.

1.04. 
SUBMITTALS

A.
The contractor shall submit, in a timely manner, all submittals for approval by the engineer.  Under no circumstances shall the contractor install any materials until the engineer has made final approval on the submittals.

B.
The engineer shall review and stamp submittals.  Work may proceed and equipment released for  fabrication after  contractor receives returned submittals stamped with  "NO EXCEPTIONS  TAKEN" or "MAKE CORRECTIONS NOTED".

C.
Shop Drawings - Shop drawings shall be submitted to the engineer for approval and shall consist of:

1. 
General assembly drawing  of  the  boiler  including  product description, model number, dimensions, clearances,  weights, service sizes, etc.
2. 
Schematic flow diagram of gas valve trains.

3. 
Schematic wiring diagram of boiler control system of the ladder- type showing all components, interlocks, etc. Schematic wiring diagram shall clearly identify factory wiring and field wiring by others.

D.
Manufacturer's Warranties: Manufacturer’s printed  warranties, as specified hereinafter, shall be submitted prior to final acceptance by the engineer.

E.
Manufacturer's Field Service: Manufacturer’s printed field service procedures and reports, as specified hereinafter, shall be submitted prior to final acceptance by the engineer. Report forms shall contain all information as required to do start-up and testing as specified in the product section.

1.05. 
SUBSTITUTIONS / MODIFICATIONS

A.  The bidder must submit in writing to the engineer any request for a proposed deviation, omission, modification, or substitution to this specification for evaluation no later than ten (10) days prior to the bid date.

B.  Technical data,  drawings, product  samples, and  complete data substantiating compliance of proposed substitution with  these specifications shall accompany a request for any substitution.

C.  No materials shall be deemed acceptable if not in strict and full compliance with these specifications.

D. All bidders must bid solely on the specified materials unless acceptance by the engineer of a deviation, omission, modification, or substitution is granted in writing to all bidders prior to the bid date.

1.06.
CERTIFICATIONS

A.  Manufacturer's Certification: The boiler manufacturer shall certify the following:

1. 
The products and systems furnished are in strict compliance with the specifications.

2. 
The  boiler,  burner, and  other  associated mechanical and electrical  equipment  have  been  properly  coordinated and integrated to provide a complete and operable boiler package.

3. 
ASME Certification in the form of ASME Stamp on the product and completed and signed data sheet.

4. 
ASME CSD-1 compliance in the form of completed data sheet.

5. 
CSA or UL Certification in the form of an affixed label to the equipment.

6. 
The specified factory tests have been satisfactorily performed.

7. 
The specified field tests have been satisfactorily performed.

B.
Contractor's Certification: The contractor shall certify the following:

1. 
The products and systems installed are in strict compliance with the specifications.

2.
The specified field tests have been satisfactorily performed.

C.
Boiler
Inspectors'
Certification:
All
boiler
inspections
during hydrostatic testing shall  be  performed  by  an  authorized boiler inspector who is certified by the National Board of Boiler and Pressure Vessel Inspectors and shall be submitted in writing prior to final acceptance by the engineer.

D.
Operation
and
Maintenance
Manuals:
Manufacturer’s
printed operation and maintenance manuals shall be submitted prior to final acceptance by the engineer.  Operation and maintenance manuals shall contain dimension and wiring drawings, product data, operating instructions, cleaning procedures, replacement parts list, maintenance and repair data, complete parts list, etc.

1.06. 
DELIVERY, STORAGE, AND HANDLING

A.
The contractor shall be responsible for the timely delivery of the equipment to the jobsite.
The contractor shall be responsible for unloading and rigging of the equipment. The contractor shall be responsible for protecting the equipment from the weather, humidity and temperature conditions, dirt, dust, other contaminants, as well as jobsite conditions during construction.

B.
Equipment shall be unloaded, handled, and stored in accordance with the manufacturer's handling and storage instructions.

C.
Responsibility of  making  freight  claims  to  be  performed by contractor or owner personnel.

PART II.   PRODUCTS

2.01 
MANUFACTURERS

A.
Contractor shall furnish and install near condensing boiler(s) with input as scheduled on the drawings and performance as noted in these specifications.

B.
Copper fin designs, cast iron or "add-on" secondary exchangers will not be considered.

2.02 
GENERAL DESCRIPTION

A.
Each unit shall be a vertical down-fired Firetube type complete with boiler  fittings and automatic controls.  The boiler, with all piping and wiring,  shall be factory package. Each boiler shall be neatly finished,  thoroughly tested and properly packaged for shipping. Boiler design and construction shall be in accordance with Section IV of the ASME Code for hot water heating boilers with a maximum working pressure of 125 PSIG. The boiler shall be UL certified as an indirect or direct vent  boiler and comply with ASME CSD-1  Code requirements.

2.03 
PERFORMANCE: BOILER SIZE AND RATINGS

A.
The capacity of each unit shall be as indicated on the drawing schedule.

B.
Exit flue gas temperature of the boiler shall not exceed  
°F

gross at maximum hot water supply temperature of  
°F and

return  temperature  of   


°F.
The boiler net output shall be BTU/Hr with  an overall fuel-to-water efficiency of %  at  high  fire  and  %  at  low  fire  at  above operating temperatures.

C.
Performance criteria:

	Output
	 
_MBTU

	Gas Input
	 
_MBTU

	Design Pressure
	 
_PSIG

	Operating Pressure
	 
_PSIG

	Heating Surface (minimum)
	 
_Sq. Ft. Fireside

	Burner Turndown Ratio
	5:1(1500-2400), 4:1(400-1000)

	Overall Efficiency (With a hot water supply tem- perature of 160 °F and return temperature of 140
°F)
	 
_% at low fire
 
_% at high Fire

	NOX Emission (maximum)
	20 PPM (corrected to 3% O2)

	Electrical
	115V / 60H / 1P

	Fan Motor
	 
Watts max

	Noise level
	70 dBA max*

	Available Gas Supply Pressure
	 
PSIG

	Weight
	Dry:_ 

Flooded:_ 


	Seismic Zone
	

	Altitude
	 
 ASL

	Code Requirements
	ASME / NATIONAL BOARD CSD-1

cULus

STATE OF  
 FACTORY MUTUAL (FM) XL-GAP


* Noise Sound Levels: Based on ABMA test code for packaged boilers measured @ 4 ½ feet vertically above the bottom of the base and 3’0” horizontally in front of the end of the burner or front surface of control cabinet. Sound levels dBA on the scale in reference to 0.0002 microbars.

2.04 
BOILER DESIGN

A.
Boiler shall be a compact, single-pass, vertical down-fired Firetube type,   with  carbon steel  tubes,  tube  sheets, and  combustion chamber.   The boiler pressure vessel shall be completely insulated with a minimum of 2” of insulation and shall be encased in an 18 gauge metal cabinet with powder coated finish.

B.
The tubes shall be carbon steel and shall be fitted with AluFer internal heat transfer fins for extended heating surface.

C. 
The top tubesheet shall be fully accessible without burner disassembly or removal from the boiler. The burner assembly shall be complete with lifting hinges and pneumatic lifters.

D.
The vessel shall  be fully  insulated with  a  minimum  of  2”  of insulation, guaranteeing external convection and  radiation heat losses to the boiler room from the boiler shall be less than 0.5% of the rated input.

E.
Boiler   shall   be   built   to   seismic   zone  requirements and manufacturer shall provide seismic calculations showing tie-down requirements for bolt diameters. Bolts and tie-down shall be by contractor.

F.
Each boiler shall be constructed in accordance with the A.S.M.E. Section IV Code and bear the “H” stamp and shall be manufactured within  an  ISO 9001  Certified facility  to  ensure high  quality standards.

G.
The boiler shall be designed for top rear water outlet and bottom rear water inlet; the water inlet (return) shall be equipped with internal baffling.  Inlet connection size shall be flanged.

Outlet connection size shall be flanged.  The maximum pressure drop through the boiler shall not exceed 0.45 psi with a 20-degree differential and less than 0.05 psi with a 60-degree differential.

H. 
A threaded air vent connection shall be furnished at the top of the boiler for field piping to an expansion tank or for the addition of an auto-vent valve when a bladder type expansion tank is utilized.

I. 
To drain the boiler, a bottom-threaded connection shall be provided at the rear side of the boiler and field piped by the installing contractor with a manual full size shutoff valve to drain.

J.
Boiler design shall permit operation with a water condition of 8.0 - 9.5 pH range.

2.05 
BURNER DESIGN

A.
General: Forced draft burner mounted in and integral with the boiler hinged  top door so when the door is opened the burner head, furnace, tubesheet, and tubes are exposed. The burner door shall utilize easy removable threaded handles, and the burner shall swing upward on hydraulic piston arms, one on each side to provide open support of the burner assembly.

B.
The burner shall be of the unitized Venturi, Gas Valve, Blower, and burner  head design. This pre-mix design shall utilize a variable speed fan connected to a venturi to simultaneously modulate fuel and air for a  minimum a 5:1 turndown ratio. The venturi design shall  also act  as  a  method for  compensating for  changes in barometric pressure,  temperature and humidity so the excess air levels are  not  adversely   affected by  changes in  atmospheric conditions.
External linkages,  damper motor drives and single speed fans shall not be acceptable.

C. 
Burner head shall be constructed of a Fecralloy-metal fiber for solid body radiation of the burner flame. Combustion shall take place on the surface of the burner mantle, which shall be constructed of a woven fecralloy  material creating a 360  degree low temperature radiant flame.

D.
Emissions:
The equipment shall  be  guaranteed to  limit  NOx emissions to 20  PPM or less. NOx emission levels shall not be exceeded at full operating conditions and at designed turndown of the  burner. Proof of such emissions certification shall be made available  to the engineer and purchaser and demonstrated at the time  of   start-up.  External flue  gas recirculation shall  not  be accepted for emission control.

E.
Gas Train  –  As  a  minimum,  the  gas  train  shall  meet  the requirements of UL and ASME CSD-1 and shall include:

1. 
Low Gas Pressure Interlock, manual reset.

2. 
High Gas Pressure Interlock, manual reset.

3. 
Upstream and downstream manual test cocks.

4. 
‘Butter Ball’ type manual shutoff valve upstream of the main gas valve.

5. 
Unibody double safety gas valve assembly.

6. 
Gas Pressure Regulator

7. 
Union connection to permit burner servicing.

F.
Combustion Air  Proving Switch  shall  be  furnished to  ensure

2.06 
BOILER TRIM

A.
Safety valve(s) shall be ASME Section IV approved side outlet type mounted on the boiler air vent outlet.  Size shall be in accordance with  code requirements and set to open at 125  psig (or less if system design pressure is lower).

B.
Temperature and pressure  gauge shall be mounted on the water outlet.

C. 
Solid state low water cut-off probe with  manual reset and test switch shall be provided.

D.
Manual Reset High Limit Temperature sensor; range not to exceed

240 0 F and shall be an integral device of the Boiler Burner Control and UL recognized as a limit control.

E.
Outlet water supply sensing probe for operating limit and modulation setpoint.

F.
Return water-sensing probe for operating limit and modulation setpoint.

2.07 
BOILER CONTROLS

A.
The Boiler  shall  include a  Falcon microprocessor-based  Boiler Burner control which shall be an integrated, solid state digital micro-processing modulating  device,  complete  with   sequence indication, fault reset, mode selection, and parameter set-point. It shall be mounted at the front of the boiler panel for easy access and viewing.

B.
Controller shall provide for both flame safeguard and boiler control through separate power supplied CPU’s (to meet NFPA) and shall perform the following functions:

1.  Burner sequencing with safe start check, pre-purge, Electronic direct spark ignition, and post purge. Flame rod or UV scanner to prove combustion.

2.  Flame Supervision. The control shall provide pre-purge and post-purge and shall maintain a running history of operating hours, number of cycles, and the most recent 15 lockouts. The control shall be connected to a color touchscreen display that will retrieve this information.

3.  Safety Shutdown with display of lockout condition.

4.  Modulating control of the variable speed fan for fuel/air input relative to load requirements.

5.  Gas pressure supervision,  high and low.

6.  Combustion Air Proving Supervision.

7.  The supply temperature and set-point temperature shall be displayed at all times on the touch screen display.

8.  Controller shall be equipped with a touch screen display for configuration set up, trouble shooting, and operational display.

9.  Include the capability to control system circulating pump and provide PID modulating control of 2 heating loops.

10. Outdoor reset control.

11. Anti-condensation routine  to  increase the  firing  rate  (and optionally shut off the pump) when the temperature is below a configurtable setpopint.

12. Remote set point / remote modulation.

13. Modbus communication capability.

C. 
All parameter input control set-points shall be factory downloaded with  jobsite conditions programmed at the time of initial jobsite operation.

D.
All controls to be panel mounted and so located on the boiler as to provide ease of servicing the boiler without disturbing the controls and also located to prevent possible damage by water according to UL requirements.

E.
Electrical power supply shall be 120 volts, 50/60 cycle, single phase for the fan and 120 volts for control circuit requirements.

F.
When multiple boilers are to be installed together, a system integration control shall be provided to stage up to 8 boilers.  The control shall include automatic selection of needed boilers based on energy demand, an adjustable outdoor reset schedule, domestic hot water priority, and a system digital display.  The control shall force each boiler to a lower fire, before allowing any boiler to operate at high fire.  This allows for inverse efficiency (lower fire rate, higher efficiency).  The control shall monitor supply water temperature, return water temperature and shall communicate between boilers via RS-485 wiring.

2.08 
BOILER FLUE VENTING

A.
The Boiler shall be UL certified as an indirect or direct vent boiler.  Venting shall be accomplished with Category III or IV vent piping installed in accordance with applicable national and local codes.

B.
For direct venting, the boiler shall have the combustion air intake supply ducted with PVC pipe from the outside. Vibration isolation components are not required.

2.09 
MANUFACTURER’S FIELD SERVICES

A.
General:
The
boiler
supplier’s
factory
authorized
service organization shall be responsible for performance of inspections, start up and testing of the package boiler, and accessory equipment and materials furnished under this Section.
A detailed written record of the start up performance, including burner setting data over the entire load range shall be furnished to the engineer before final acceptance. All labor, equipment, and test apparatus shall be furnished by the authorized service organization. All equipment defects discovered by the tests shall be rectified either by the service organization or boiler manufacturer.

B.
Equipment inspection: Boiler representative to provide  
hours of jobsite assistance to inspect boilers and other equipment upon arrival, verifying completeness of equipment supplied and potential damages. All shipped loose components, such as safety valves, to be mounted on boiler by boiler provider after contractor has set boiler in building.

C.
Pre start-up walk through: Boiler representative  shall spend   
 hours at jobsite reviewing installation with mechanical contractor to be conducted approximately 1 week prior to startup.

D.
Start-up shall be conducted by experienced and factory authorized technician in  the regular employment of the authorized service organization, and shall include the following:

1. 
Demonstrate  that boiler, burner, controls, and accessories comply with requirements of this Section as proposed by the boiler  and accessories supplier.
Pre-test all items prior to scheduling the final testing that will be witnessed by the test engineer.

2. 
Readings at different firing rates (20, 50, 75 and 100%) of load for the modulating burner shall be taken with a written report of  the tests submitted to the engineer.
The reports shall include readings for each firing rate tested and include stack   temperatures, O2,  CO,  NOx,  and  overall  boiler efficiency.

3. 
Auxiliary Equipment and Accessories: Observe and check all pumps, valves, draft fans,
electric
motors
and other purtenant equipment during the operational and capacity tests for leakage, malfunctioning, defects, and non compliance with  referenced  standards or overloading as applicable.

4. 
Commissioning Requirements:

a. Fireside inspection

b. Set up fuel train and combustion air system c. Set up operating set points

d. Check all safeties, including flame safeguard, LWCO, airflow, fuel pressures, high limits.

g. Set up and verify efficiencies at 20%, 50%, 75%, and 100%

h. Set up and verify burner turndown.

E.
Training to include all safety procedures, maintenance procedures, control operations, and diagnostic procedures. Training to be provided in a single hour continuous session to accommodate operator’s availability on site.

2.10 
OPERATING & MAINTENANCE MANUALS

A.
Provide two (2) Operating and Maintenance manuals including cut- away views of boiler and burner, schematics including fuel trains, general  instructions for maintenance and  inspections, complete spare parts lists and trouble shooting procedures.

B.
A wiring diagram corresponding to the boiler shall be affixed to the boiler near the electrical panel.

2.11 
WARRANTY DATA

A.
The pressure vessel shall be guaranteed against thermal shock for 5 years when utilized in a closed loop hydronic heating system with a temperature differential of 100 °F or less.

B.
All parts not covered by the above warranties shall carry a 1 year warranty from startup, or 18  months from shipment, whichever occurs first.  This shall include all electrical components and burner components.

PART III.  EXECUTION
3.01 
GENERAL

Installation shall be provided by the contractor in accordance  with the requirements of the codes specified hereinbefore. All of the contractor's work  shall be performed by experienced personnel previously engaged in boiler plant construction and shall be under the supervision of a qualified installation supervisor.

3.02. INSTALLATION

A.
Install equipment in strict compliance with manufacturer's installation instructions.

B.
Install equipment in strict compliance with state and local codes and applicable NFPA standards.

C.
Maintain manufacturer's recommended clearances around sides and over top of equipment.

D.
Install components that were removed from equipment for shipping purposes.

E.
Install components that were furnished loose with equipment for field installation.

F.
Provide all interconnecting electrical control and power wiring. G.
 Provide all fuel gas vent and service piping.

H. 
Provide all piping for boiler pipe connections.

3.03. 
FIELD TESTING
A.
The manufacturer’s representative  shall test all boiler and burner interlocks, actuators, valves, controllers, gauges, thermometers, pilot lights,   switches, etc.
Any  malfunctioning component shall  be replaced at the time of initial start-up if found to be inoperative.

B.
All adjustments to boiler, burner, and boiler control system shall be performed by the manufacturer’s authorized service representative.

3.04. 
START-UP, INSTRUCTION AND WARRANTY SERVICE
A.
The
manufacturer’s
representative
shall
provide
start-up
and instruction of each new boiler, including burner and boiler control system as specified herein.  Start-up and instruction shall cover all components assembled and furnished by the manufacturer whether or not of his own manufacture.

Warranty service shall be in accordance with the manufacturer's warranty statement unless other provisions have been agreed to during project bidding.























B9-1
Rev. 11-10

