# SAMPLE SPECIFICATIONS - MODEL 4WI STEAM BOILERS

  - PART 1 	GENERAL

### 1.1 	SCOPE

A.	The work to be performed consists of providing all labor, equipment, materials, etc. to furnish and install new factory assembled steam boiler(s) as described in the specifications herein.

### 1.2 	REFERENCES

A.	Product Data: Include rated capacities; shipping, installed, and operating weights; furnished specialties; and accessories for each model indicated.

B.	Shop Drawings: Detail equipment assemblies and indicate dimensions, required clearances, and method of field assembly, components, and location and size of each field connection.

C.	Wiring Diagrams: Detail wiring for power, signal, and control systems and differentiate between manufacturer-installed and field-installed wiring.

D.	Source Quality Control Tests and Inspection Reports: Indicate and interpret test results for compliance with performance requirements before shipping.

E.	Field Test Reports: Indicate and interpret test results for compliance with performance requirements.

F.	Maintenance Data: Include parts list, maintenance guide, and wiring diagrams for each boiler.

G.	ASME Section I or IV (Power boilers or Heating Boilers)

H.	NSI Z21.13 (Gas Fired Low Pressure Boilers)

I.	NFPA 54 (ANSI Z221.3) National Fuel Gas Code

J. 	Factory Mutual

K.	ASME CSD-1 (Controls and Safety Devices)

L.	XL-GAP (formerly GE-GAP GE Global Asset Protection)

M.	UBC (Uniform Building Code)

N.	MC (Uniform Mechanical Code)

O.	NEC (National Electrical Code)

P.	UL (Underwriters Laboratories)

Q.	NFPA 85

### 1.3 	QUALITY ASSURANCE

A.	The equipment shall, as a minimum, be in strict compliance with the requirements of this specification and shall be the manufacturer’s standard commercial product unless specified otherwise. Additional equipment features, details, accessories, appurtenances, etc. which are not specifically identified but which are a part of the manufacturer’s standard commercial product, shall be included in the equipment being furnished.

B. 	The equipment shall be of the type, design, and size that the manufacturer currently offered for sale and appears in the manufacturer’s current catalogue. The equipment shall be new and fabricated from new materials and shall be free from defects in materials and workmanship.

C.	The equipment must fit within the allocated space, leaving ample allowance for maintenance and cleaning, and must leave suitable space for easy removal of all equipment appurtenances. Tube pull clearance space from either the front or rear of boiler must be maintained.

D.	All units of the same classification shall be identical to the extent necessary to insure interchangeability of parts, assemblies, accessories, and spare parts wherever possible.

E. 	In order to provide unit responsibility for the specified capacities, efficiencies, and performance, the boiler manufacturer shall certify in writing that the equipment being submitted shall perform as specified. The boiler manufacturer shall be responsible for guarantying that the boiler provides the performance as specified herein.

### 1.4 	SUBMITTALS

A.	The contractor shall submit, in a timely manner, all submittals for approval by the engineer. Under no circumstances shall the contractor install any materials until the engineer has made final approval on the submittals.

B.	The engineer shall review and stamp submittals. Work may proceed and equipment released for fabrication after contractor receives returned submittals stamped with "NO EXCEPTIONS TAKEN" or "MAKE CORRECTIONS NOTED".

C.	The bidder must submit in writing to the engineer any request for a proposed deviation, omission, modification, or substitution to this specification for evaluation no later than ten (10) days prior to the bid date. A request for any substitution shall be accompanied by technical data, drawings, product samples, and complete data substantiating compliance of proposed substitution with these specifications. No materials shall be deemed acceptable if not in strict and full compliance with these specifications. All bidders must bid solely on the specified materials unless acceptance by the engineer of a deviation, omission, modification, or substitution is granted in writing to all bidders prior to the bid date.

D.	Shop Drawings - Shop drawings shall be submitted to the engineer for approval and shall consist of:

E.	General assembly drawing of the boiler including product description, model number, dimensions, clearances, weights, service sizes, etc.

F.	Schematic flow diagram of gas valve trains.

G.	Schematic wiring diagram of boiler control system of the ladder-type showing all components, all interlocks, etc. Schematic wiring diagram shall clearly identify factory wiring and field wiring.

H.	Installation Instructions: Manufacturer’s printed instructions for installation shall be submitted to the engineer for approval.

I.	Manufacturer’s Warranties: Manufacturer’s printed warranties, as specified hereinafter, shall be submitted prior to final acceptance by the engineer.

J.	Manufacturer’s Field Service: Manufacturer’s printed field service procedures and reports, as specified hereinafter, shall be submitted prior to final acceptance by the engineer. Report forms shall contain all information as required to do start-up and testing as specified in the products section.

### 1.5 	CERTIFICATIONS

A.	Manufacturer’s Certification: The boiler manufacturer shall certify the following:

1.	The products and systems furnished are in strict compliance with the specifications.

2. 	The boiler, burner and other associated mechanical and electrical equipment have all been properly coordinated and integrated to provide a complete and operable boiler.

3. 	ASME certification.

4. 	UL and CSD-1 certification.

5. 	The equipment furnished has been installed in accordance with the manufacturer’s installation instructions.

6. 	The specified factory tests have been satisfactorily performed.

7. 	The specified field tests have been satisfactorily performed.

B. 	Contractor’s Certification: The contractor shall certify the following:

1. 	The products and systems installed are in strict compliance with the specifications.

2. 	The specified field tests have been satisfactorily performed.

C.	Boiler Inspectors’ Certification: All boiler inspections during hydrostatic testing shall be performed by an authorized boiler inspector who is certified by the National Board of Boiler and Pressure Vessel Inspectors and shall be submitted in writing prior to final acceptance by the engineer.

D.	Test Reports: Factory and field test reports as described above and as specified hereinafter, shall be submitted prior to final acceptance by the engineer.

E. 	Operation and Maintenance Manuals: Manufacturer’s printed operation and maintenance manuals shall be submitted prior to final acceptance by the engineer. Operation and maintenance manuals shall contain shop drawings, product data, operating instructions, cleaning procedures, replacement parts list, maintenance and repair data, complete parts list, etc.

### 1.6 	DELIVERY, STORAGE, AND HANDLING

A.	The contractor shall be responsible for the timely delivery of the equipment to the job site. The contractor shall be responsible for unloading and rigging of the equipment. The contractor shall be responsible for protecting the equipment from the weather, humidity and temperature conditions, dirt, dust, other contaminants, as well as job site conditions during construction.

B. 	Equipment shall be unloaded, handled, and stored in accordance with the manufacturer’s handling and storage instructions.

C.	The work to be performed consists of providing all labor, equipment, materials, etc. to furnish and install new factory assembled, low pressure hot water boilers as described in the specifications herein.

  - PART 2 	PRODUCTS

### 2.1 	MANUFACTURERS

A.	Contractor shall furnish and install Cleaver Brooks Model 4WI natural gas (combination Gas/Oil fired) steam boiler(s) with design pressure as scheduled on the drawings.

B.	Alternate manufacturers complying with plans and specifications must be submitted and approved by the consulting engineer within 10 days prior to bid date.

### 2.2 	GENERAL DESCRIPTION

Factory packaged unit shall include boiler, burner, heavy duty skids, painted steel jacket with two inches of fiberglass insulation, controls and accessories all piped and wired for single point field connections. Units shall carry packaged label of Underwriters Laboratory (UL) and be in accordance with ASME/CSD-1, all codes required by the local governing authorities and as indicated on the design performance data sheet. A certified factory fire-test shall be provided on all fuels with data sheets furnished to Engineer and Owner. ASME certified, labeled, stamped and designed for _____ PSIG steam in accordance with Section (I or IV) of ASME Code. Unit shall be designed to Seismic Zone requirements and be provided with tie down clips and calculations showing bolt diameter requirements. Manufacturer’s Representative to provide services for field testing and adjusting of boiler and controls to meet design requirements.

### 2.3 	PERFORMANCE: BOILER SIZE AND RATINGS

A.	The capacity of each unit shall be indicated on the drawing schedule.

B.	Performance Criteria:

Performance Criteria

Manufacturer:	CLEAVER-BROOKS

Model:	Promethean Line

Horsepower: 	_____ HP

Output:	_____ #/hr (from and at 212°F)

Gas Input: 	_____ MBH

Oil Input:	_____ GPH

Design Pressure: 	_____ PSIG

Operating Pressure	_____ PSIG

Steam Disengaging Area (minimum) 	_____ Sq. Inches

Steam storage area (minimum) 	_____ Cu. Ft.

Heating Surface (minimum):	_____ Sq. Ft. Fireside

Heating Release (maximum):	_____ BTU/Cu. Ft

Burner Turndown Ratio Natural Gas:

Overall Efficiency (Fuel to Steam)

Natural Gas (%): 	_____ % at High Fire

No. 2 Oil (%):	_____ % at High Fire

NOX Emission (maximum)

Gas (Natural):	_____ PPM (corrected to 3%O2)

Oil (No. 2):	_____ PPM (corrected to 3%O2)

CO Emissions (maximum)

Gas (Natural):	_____ PPM (corrected to 3%O2)

Oil (No. 2):	_____ PPM (corrected to 3%O2)

Electrical: 	_____ V / _____H / _____P

Fan Motor:	_____ HP

Air Compressor Motor: 	_____ HP

Oil Pump Motor:	_____ HP

Noise Level (3' from burner): 	_____ dBA

Available Gas Supply Pressure:	_____ PSIG

Weight

Dry: 	_____

Flooded:	_____

Seismic Zone: 	_____

Altitude:	_____ ASL

Code Requirements:	ASME / NATIONAL BOARD 
	CSD-1 NFPA 8501
	Underwriter’s Lab (UL) 
	State Of _____
	Factory Mutual (FM)
	Industrial Risk Insurers (IRI)

C.	Noise Sound Levels: Based on ABMA test code for packaged boilers measured 4-1/2 feet vertically above the bottom of the base rail and 3'0" horizontally in front of the end of the blower motor or front surface of control cabinet. Sound levels dBA on the scale in reference to 0.0002 microbars.

High Fire	#2 oil 	dBA

Low Fire	#2 oil 	dBA

High Fire	Nat Gas	dBA

Low Fire	Nat Gas	dBA

### 2.4 	BOILER DESIGN

A.	Four pass steel scotch marine firetube boiler for positive pressurized firing with forced draft burner. Wet back design with a minimum five (5) square feet of heating surface per boiler horsepower. Front and rear doors shall be davited and sealed with tad-pole gaskets using heavy duty cap screws threaded into replaceable brass nuts. When opened, doors shall expose all tubes, tubesheets and furnace for ease of inspection and maintenance. Lifting loops shall be provided. Rear door shall be refractory lined with air cooled observation port. Tubes shall be rolled, beaded and/or welded into tube sheets and tubes shall be cleanable and removable from either front or back. Tubes shall be a minimum 2.5" O.D., with a tube wall thickness of not less than .095".

B.	The boiler pressure vessel shall be completely insulated with a minimum of 2" of insulation and shall be encased in an 18 gauge metal cabinet with primer and finish coat of paint.

### 2.5 	BURNER DESIGN

A.	GENERAL: Forced draft burner mounted in and integral with boiler hinged front boiler door so when door is opened burner head, furnace, tubesheet and tubes are exposed; reversed curve cast aluminum blower fan; motor(s); ACCU-LINK single point positioning system consisting of rotary air damper located on fan discharge, straight line linkage and characterized cams; air flow switch; fuel trains and control panels. To conform to UL and other insurance requirements as indicated.

B.	GAS BURNER: Shall be of the high radiant multi-port type for natural gas. Minimum pilot safety burner shall consist of gas-electric spark ignition with 100% safety shut-off pilot, solenoid gas valve, pressure regulator and shut-off cock. Minimum main gas train shall include manual shut- off valve, pressure regulating valve, dual safety gas valves, manual test valve high-low pressure switches, manifold pressure gauge and butterfly gas valve with (14) point characterized cam assembly. Gas train shall be factory packaged to meet insurance requirements as indicated. Gas turn down shall be minimum _____. 4:1 up to 200 HP, 10:1 from 250 HP and above.

C.	OIL BURNER Oil burner shall be of the low pressure air atomizing type for No. 2 oil. Minimum pilot safety burner shall consist of gas-electric spark ignition with 100% safety shut-off pilot, solenoid gas valve, pressure regulator and shut-off cock. Oil train shall consist of retractable nozzle with flexible hoses; gauges, manifold block; air purge valve; fuel-oil controller with (14) point characterized cam assembly; dual oil solenoids; temperature switch, air compressor assembly and oil pump assembly. (For heavy oil, an oil preheat system shall be provided to include a water to water to oil safety type preheater and thermostatically controlled electric preheater.) Oil train shall be factory packaged to meet insurance requirements as indicated. Oil turn down shall be minimum 8:1(250 hp-800 hp), 4:1 (up to 200 hp).

D.	COMBINATION BURNER: Provide gas-oil fuel selector switch to provide fuel switch over without any required adjustments to burner linkage.

E.	FUEL-AIR CONTROL: Modulating fire with proven low fire start. Provide manual potentiometer with manual-auto switch on boiler control panel in addition to automatic fuel-air controller. Linkage system shall be Cleaver-Brooks ACCU-LINK single point positioning with rotary air damper, linkage and (14) point characterized cam assembly for all fuels. Provide automatic operating control and manual reset high limit.

F.	FORCED DRAFT BLOWER: All air for combustion shall be supplied by a blower mounted in the front boiler door above the burner. The Backward curved cast aluminum radial impeller shall be directly connected to a flanged type ODP motor. This rigid mounting with the blower wheel inside the head shall eliminate vibration and reduce noise level. The balanced blower wheel shall be cast aluminum with radial blades. The combustion air damper shall be an integral rotating damper and shall be automatically adjusted for proper air quantity by a mod motor to maintain proper fuel-air ratios.

G.	EMISSION CONTROL: Boiler NOx shall be furnished with guaranteed internal induced NOx control for 60 PPM (30, 15 & <9 PPM NOx systems are optional) corrected to3% 02 over the entire turndown range. Boiler capacity, turndown, flame stability and efficiency shall not be affected by the internal NOx control. External FGR piping shall not be allowed. Low NOx system shall be part of the Boiler/Burner UL package label and manufacture shall have Twelve (12) years of emission control experience in the state of _____.

### 2.6 	BOILER TRIM

A.	To include the following:

1.	_____" diameter pressure gauge.

2. 	ASME safety relief valve(s).

3. 	Auxiliary Low Water Cutoff, Warrick 3C-2.

4. 	Primary low water cut-off.

5. 	Operating control.

6. 	Limit control with manual reset.

7.	_____" stack thermometer.

8. 	Feedwater regulating valve with 3 valve bypass

9. 	Low fire hold controller (optional).

10.	1 Slow Opening Blowdown Valve, Size _____", Class 200#

11.	2 Quick Opening Blowdown Valves, Size _____", Class 490#

12.	Feedwater Globe Valve, Size _____", Class 240#

13.	1 Feedwater Check Valve, Size _____", Class 240#

14.	1 ASME Spool Piece, Inlet Size _____", Outlet Size______", Length ______"

15.	1 Stop Valve (Steam Header Valve), Size _____", Flanged, Cast Iron, Class 250"

16.	1 Stop Check Valve (Non-Return Valve), Size _____", Flanged, Cast Iron, Class 250", Straight Pattern, with Free Blow Drain Valve

17.	Factory mounted, installed, tested, and certified piping (by A, S, or PP ASME stamp holder) and valves per ASME Code, including:

Water Column piping

Bottom Blowdown (from boiler to last code valve)

Feedwater assembly (shipped loose)

Surface Blowdown piping with stop valve and metering valve.

18.	Modulating Feedwater Control Valve, including 3-Valve Bypass

19.	Oil Pump, Mounted and Wired

20.	Air Atomizing Compressor, Mounted and Wired

21.	Platforms and ladder to access steam header and safety relief valves. Built to OSHA requirements.

B.	WATER COLUMN/LOW WATER CUTOFF AND WATER LEVEL CONTROL SYSTEM (150-250 psig design): Shall be a CB LEVEL MASTER Water level control system and shall be comprised of a microprocessor-based electronic controller, a non-contact, non-wearing, continuously reading absolute level sensor and pressure chamber. The control system shall be designed as follows: The electronic controller shall be mounted in the common control panel and operate in ambient temperatures from 32 degrees F to 125 degrees F, the pressure chamber shall be boiler mounted and operate to pressures of 250 psig and the level sensor shall operate to pressures of 250 psig and temperatures to 400 degrees F. The pressure containing components shall be constructed in accordance with ASME Code. A shielded, four conductor cable with ground shall be run in metal conduit between the level sensor and the controller. Supply power shall be 115VAC-1 phase- 60 Hz. All wiring shall be in compliance with the National Electrical Code.

The pressure chamber shall have a sight glass mounted on the side. The level sensor shall have an accuracy of .01" or greater. The electronic controller shall have level and error indicating lights, alphanumeric display for messaging, reset/menu switch and the following features:

1. 	Continuous Level Indication

2. 	Low Water Cutoff & Alarm

3. 	High Water Alarm

4. 	Low & High Water Warning

5. 	Full Modulating Control of Modulating Feedwater Control Valve

6. 	Continuous Monitoring of Float Operation

7. 	Column Blowdown Detection and Reminder

8. 	Auto or Manual Reset

9. 	Real Time Clock

10. Alarm Annunciation

11. Alarm History Files with Time Stamp

12. Water Column Blowdown Record

13. Auxiliary Low Water Cutoff Check

14.	RS 232 Interface

15.	Maximum Contacts Rating 15 amps Resistive Load

### 2.7 	BOILER CONTROLS

A.	A common enclosure shall house the control panel and the entrance panel. Enclosure shall be NEMA 4 rated and shall be mounted at the side of the boiler in a location convenient to the operator. Enclosure shall consist of upper and lower sections divided by a partition with a separate hinged door for each section. Upper section (low voltage) will house boiler controls including flame safeguard, water level system controller, and Hawk ICS if so equipped. Lower panel section (high voltage) will house entrance panel.

B.	OPTION 1) BURNER MANAGEMENT SYSTEM (CB 780E Standard): Mounted at side of boiler in control panel enclosure. Microprocessor-based control to monitor all critical boiler and burner interlocks control and supervise burner light off sequence, and initiate an orderly safety procedure in the event of interlock or flame failure. Dynamic self checking. System to provide pre-post purge status, fault history, and diagnostic information by means of a two-line alpha-numeric display with alarm/status LEDS.

C.	(OPTION 2) CB-HAWK ICS Boiler Control Sstem (Optional upgrade): Integrated Boiler Control and Management System:

Boiler shall be factory equipped with a Boiler Control System combining a Digital Burner

Management System for flame safety, and a Programmable Logic Controller for boiler modulation and operator interface functions.

The factory pre-configured Boiler Control System shall integrate the Burner Management functions and the PLC based modulation and operator interface functions. The logic of the Burner Management System and the modulating controls will not be run in the same processor or powered by the same DC supply. The PLC and Operator Interface Hardware shall be as manufactured by Allen Bradley.

Major system components shall include:

•	Programmable Logic Controller

•	Touch Screen HMI

•	One Burner Management Controller with Wiring Sub-Base

•	One Flame Scanner and amplifier

•	Various Temperature and Pressure Sensors

Major functions provided by the Boiler Control System shall be:

•	Automatic sequencing of the boiler through standby, pre-purge, pilot flame establishing period, main flame establishing period, run, flame proving and lockout and post-purge

•	Full modulating control of fuel and air

•	Utilize solid state controls and sensors to provide various control functions, such as:

Modulating control (algorithm shall be Proportional-lntegral-Derivative (PID) type)

Thermal shock protection

High and Low limit alarms and shutdowns

•	Touch Screen graphical operator interface and monitoring

Manual control of the boiler firing rate using control screens on the HMI to increment or decrement the firing rate

On screen indication of burner management controller status and diagnostics

On screen display of system alarms and faults

On screen history of alarms and faults

On screen recommendations for troubleshooting of fault conditions

On screen water level indication and alarm(s)

•	Stack Flue Gas, Combustion Air and Shell (water) temperature indication

•	Boiler efficiency calculation

•	Low Fire Hold with Minimum Temperature Control

•	Assured Low Fire Cut-Off (ALFCO)

The Boiler Control System shall incorporate the following safety provisions:

•	Examine all load terminals to assure it is capable of recognizing the true status of the external controls, limits and interlocks. If any input fails this test, the Burner Management System shall lockout on safety shutdown.

•	Closed-loop logic test of critical loads (ignition, pilot and main fuel valves) and must be able to lockout on safety.

•	Pre-ignition interlocks (fuel valve proof of closure, etc.) and flame signal checked during Standby and Pre-Purge.

•	Dynamic checking of the flame signal amplifier.

•	Safe start check and expand check to include monitoring flame signal during standby.

•	High and Low fire switches checked for proper sequencing.

The Boiler Control System shall provide the ability to communicate with external digital via Ethernet as a standard. OPC compliant Internet communications shall be supported, with the Boiler Control System supplied with its own IP address.

### 2.8 	SHOP TEST

A.	Shop test: The complete packaged boiler shall receive factory tests to check construction and function of all controls. All shop tests may be witnessed by the purchaser at his own c upon sufficient notice to the company.

### 2.9 	ACCESSORIES - BOILER FLUE VENT

### 2.10	ACCESSORIES - FEEDWATER SYSTEM (BOILER FEEDSET OR DEAERATOR)

### 2.11	ACCESSORIES - FEEDWATER HEATER OR ECONOMIZER

### 2.12	ACCESSORIES - BLOWDOWN SEPARATOR AND/OR BLOWDOWN HEAT RECOVERY

### 2.13	ACCESSORIES – O2 TRIM SYSTEM

### 2.14	ACCESSORIES - CHEMICAL FEED SYSTEM AND/OR WATER TREATMENT

### 2.15	MANUFACTURER FIELD SERVICES

A.	General: The boiler and accessories supplier shall be responsible for performance of inspections, start up and testing of the package boiler and accessory equipment and materials furnished under this section. A detailed written record of the start up performance, including burner setting data entire load range shall be furnished to the test engineer before test personnel leave the site. Equipment and test apparatus shall be furnished by the supplier. All equipment defects discovered by the tests shall be rectified. The minimum time for two (2) boilers is five (5) days.

B.	Equipment inspection: Boiler representative to provide _____hours of job site assistance to inspect boilers and other equipment upon arrival, verifying completeness of equipment supplied or damages. Responsibility of making freight claims to be performed by contractor or owner personnel.

C.	Pre start-up walk through: Boiler representative shall spend _____ hours at job site reviewing with mechanical contractor to be conducted approximately 1 week prior to startup.

D.	Start-up shall be conducted by experienced and factory authorized technician in the regular employment of the boiler supplier, and shall include:

1.	Demonstrate that boiler, burner, controls and accessories comply with requirement Section as proposed by the boiler and accessories supplier. Pre-test all items prior to scheduling the final testing that will be witnessed by the test engineer.

2.	Readings at different firing rates (25, 50, 75 and 100%) of load for the modulating burner shall be taken with a written report of the tests submitted to the test engineer. The reports shall include readings for each firing rate tested and include stack temperatures, O2, CO, NOx and overall boiler efficiency.

3.	Auxiliary Equipment and Accessories: Observe and check all valves, draft fans, electric motors and other accessories and appurtenant equipment during the operational and capacity tests for leakage, malfunctioning, defects, and non compliance with referenced standards or overloading as applicable.

4.	Commissioning Requirements:

a).	Fireside inspection

b).	Waterside inspection

c)	Closing and resealing of doors, manways and hand holes

d).	Set up fuel train and combustion air system

e)	Set up operating set points

f)	Check all safeties, including: Flame safeguard, LWCO, ALWCO, Air flow, Fuel pressures, High limits

g).	Set up and verify efficiencies at 25%, 50%, 75%, and 100%

h)	Set up and verify burner turndown.

I)	Set up and verify feedwater/level controls

j).	Set up and verify Emissions Compliance

E.	Training to include all safety procedures, maintenance procedures, control operations, and diagnostic procedures.

Training to be provided in a single _____ hour continuous session to accommodate operator’s availability on site.

### 2.16 	OPERATING & MAINTENANCE MANUALS

A.	Provide two (2) Operating and Maintenance manuals including cut-away views of boiler and burner, schematics including fuel trains, general instructions for maintenance and inspections, complete spare parts lists and trouble shooting procedures.

B.	A wiring diagram corresponding to the boiler shall be affixed to the boiler near the electrical panel.

### 2.17	WARRANTY DATA

A.	The entire boiler/burner package shall be guaranteed and warranted by the boiler manufacturer. Warranty shall include all parts for a period of (12) months from the date of start-up or beneficial use or 18 months from shipment, whichever comes first.

  - PART 3 	EXECUTION

### 3.1 	GENERAL

A.	Installation shall be provided by the contractor in accordance with the requirements of the codes specified hereinbefore. All of the contractor’s work shall be performed by experienced workman previously engaged in boiler plant construction and shall be under the supervision of a qualified installation supervisor.

### 3.2 	INSTALLATION

A.	Install equipment in strict compliance with manufacturer’s installation instructions.

B.	Install equipment in strict compliance with state and local codes and applicable NFPA standards.

C.	Maintain manufacturer’s recommended clearances around sides and over top of equipment.

D.	Install components that were removed from equipment for shipping purposes.

E.	Install components that were furnished loose with equipment for field installation.

F. 	Provide all interconnecting electrical control and power wiring.

G. 	Provide all fuel gas vent and service piping.

H. 	Provide all piping for boiler pipe connections.

### 3.3 	FIELD TESTING

A. 	The manufacturer’s representative shall test all boiler and burner interlocks, actuators, valves, controllers, gauges, thermometers, pilot lights, switches, etc. Any malfunctioning component shall be replaced.

B. 	All adjustments to boiler, burner, and boiler control system shall be performed by the manufacturer’s representative.

### 3.4 	START-UP, INSTRUCTION AND WARRANTY SERVICE

The manufacturer’s representative shall provide start-up and instruction of each new boiler, including burner and boiler control system as specified herein. Start-up and instruction shall cover all components assembled and furnished by the manufacturer whether or not of his own manufacture.