SAMPLE SPECIFICATIONS

ELECTRODE STEAM BOILER MODEL CEJS SPECIFICATION

Provide High Voltage Electrode Steam Boiler for operation on  	_KV PH, 4 wire,

HZ. Boiler rating shall be  	PSI and shall be designed for operation at

PSI steam  pressure,  	_MW capacity.

1.0 Design	The boiler design shall consist of a pressure  vessel having a central column from which water, under pressure,  is forced through nozzles toward the several electrodes which surround the column. Steam is generated  from the surface of the several streams  of water by heat generated  as the electrical current flows from the electrode to the central column and through the stream  of excess water as it falls from the electrode to a grounded “counter electrode” on its way back to the bottom of the boiler.

All streams  of water originating in the central column shall be identical in shape based  on pressure maintained  in the central column therefore avoiding steam  and interference droop causing splashing and potential electrical short leading to shut- down.

There shall be an upper level man-way(s) allowing a visual initial adjustment of stream shape  by varying the speed of the boiler pump (see 2.1.4) to establish  suit- able pressure  in the central column for internal distance  based  on voltage spacing.

Regulation of the boiler output shall be accomplished  by a movable load regulating shield which prevents part or all of the nozzle streams  from coming into contact with the boiler electrodes.  The position of the load regulating shield will be regulated by the boiler controls to maintain the desired steam pressure or to prevent the boiler from drawing more than the desired kilowatts when the steam requirements  exceed the boiler capacity. The boiler electrodes shall be located entirely in the boiler steam space so that stopping of the boiler pump will cause  the boiler to shut down. Regu- lation of the boiler capacity shall be from 100% to 0% without the necessity of interrupting the high voltage supply.

2.0 The Boiler

Component Parts

2.0.1 Boiler Shell

The boiler shall be a single shell, vertical type. The shell shall be constructed  and stamped  in accordance  with the ASME Boiler & Pressure  Vessel Code, and shall carry a National Board Pressure  Vessel Registration Nameplate.

The shell design (and stamped)  pressure  rating shall be   PSI for operation at   PSI. A man-way 355mm x 457mm (14" x 18") shall be provided for access  to the boiler

interior for internal inspection and repair/replacement of internal parts.  A second

man-way

305mm x 380mm (12" x 16") shall be provided at the upper level for inspection of the jets. No other access  is required for inspection or service. All boiler connections over 50mm  (2") pipe size shall be flanged.

2.0.2 The Central Column and Nozzle Stock Plates

The central column and nozzle stock, through which water is conducted  to the stream nozzles, is fabricated from mild steel and supported  from the top of the boiler.

For optimum water stream shape,  each nozzle has a conical collector cone leading to a round pipe with a cross insertion forming straightening  vanes. This design pro- duces a sharply defined water stream from each nozzle.

The stream nozzles are inserted into bolted, removable plates to allow replacement or cleaning without removal of the nozzle stock from the boiler. Nozzle rows shall be horizontally slanted for smooth progressive interception and capacity control.

The pump shall deliver its full output to the nozzle stock at all times and maintain a constant  static head inside the nozzle stock to assure that at no time during boiler operation will any stream nozzle have less than 15' of liquid static head supply pressure.

2.0.3 Electrode Boxes and Target Plates

Electrode boxes have 3 closed sides terminating in rounded edges.

Target Plates are removable and reversible with round bars facing the jet streams for smooth contact  and no splashing.  Water then flows smoothly in the formed grooves to a collection at the bottom of the box.

The bottom of the box is solid steel with machined  holes with cross insertion to form the steams  of water toward the counter electrode.

2.0.4 Counter Electrodes

Counter electrodes shall be made of solid steel plate with machined  holes matching the holes in the bottom of the electrode box for smooth flow in order to avoid splashing.  Solid welded bracket for attaching  to boiler shell.

2.0.5 Insulators and Power Rods

Each electrode box is supported  by the high voltage power rod. Power rods insulat- ing tubes shall be quartz - 25KV class.

Insulators shall be 25KV class high grade aluminum,  9 skirts for long tracking path, coated,  for maximum protection and reliability.

The internal insulator shall be protected  by stainless  steel steam  throttling shield and rated for 750PPM alkalinity.

The external insulator shall be identical 25KV class coated insulator in order to offer maximum protection against deposits on skirts due to air contaminants in boiler room atmosphere.

2.0.6 The Load Regulating Shield 0-100%

The load regulating shield shall be concentric with the central column and will be supported  by a yoke and rod extending through the top of the boiler to the load reg- ulating mechanisms.The upper rim of the load regulating shield shall incorporate a stainless  steel "knife" edge to intercept the flow from the water nozzles in a manner which will minimize the disturbance  to the nozzle streams  which are above the shield. This sharp edge shall be able to split the capacity of a stream for maximum

accuracy in capacity control and without loss of quality or excessive splashing.  A shield position Indicator shall be included in the control system.  Boiler will be fur- nished with a hydraulic cylinder, pump and control system to control shield position according to demand  between 0% and 100%.

2.0.7 Boiler Circulating Pump(s) on separate skid

The boiler circulating pump(s) shall be a centrifugal type rated for continuous  duty at the boiler operating pressure and temperature and shall be selected for low NPSH and to deliver the flow and head required for proper operation of the boiler. The pump shall be coupled to the boiler with suitable piping spools, flanges and a man- ually set butterfly valve.

The pump shall incorporate a single mechanical  seal with water cooling. Pump motors shall be sized for maximum pump horsepower requirements  and to be stan- dard shaft, T.E.F.C., foot mounted,  and readily available. The pump will be belt- driven or VSD driven, allowing for a simple initial adjustment to maintain a steady pressure in the central column and therefore of the shape  of the parallel water jets.

2.0.8 Standby Heater

The boiler will be supplied with an immersion type flanged heating element assem- bly rated at  	V,  	Ph,  	Hz for use in maintaining the boiler at desired pres- sure when the boiler is not being used to generate steam.  The standby heater shall be controlled by two pressure  set points and by the "Standby-Run".

2.0.9 Steam Water Preheater

A steam injection preheater  has been provided for quicker heating of the "cold" boiler water after a shut-down.  It will bring the boiler to "stand-by" condition by using an outside source of steam  to heat the water and generate steam  in the isolated boiler. This procedure is manually controlled by a hand valve.

2.1 Boiler Control

System

2.1.1 Pressure and Load Controls and associated Control Panel

The boiler control system shall incorporate processor pressure control and ampere load control in the primary control system in a manner  which will permit the boiler to maintain  the desired steam  pressure so long as the steam  demand  does not exceed the desired maximum KW limit and at such times as the demand  exceeds the rating, to regulate the boiler output to the desired maximum. The maximum allowable KW rating will be adjustable  by the operator to ratings of 100% maximum to 5% minimum.  The boiler will regulate the output from 0% to 100% as required by the pressure control. Boiler will utilize "split" streams  to attain step-less  control that is linear over entire output range of the boiler. Stable regulation shall be possi- ble from 100% output down to zero load.

Controls shall be provided so electrodes  are energized before water is supplied to electrodes.  Boiler shall always start at zero load.

2.1.2 Standby-Run Control

The boiler shall incorporate a Standby-Run  control which, when in “Standby”, will manually override the Pressure  and Load controls to cause  the Load Regulating

Shield to go to the “No Output” position and simultaneously  energize the Standby Heater control circuit and de-energize the conductivity control and surface blow- down. When the Standby-Run Control is returned to “Run”, the boiler will resume normal operation starting at “0” load. This operation can also be remotely con- trolled.

2.1.3 Limit Controls

The boiler shall be equipped  with limit controls to shut down the boiler in event of occurrence of any of the following conditions: (1) excess pressure;  (2) low water; (3) high water; (4) sudden  pressure drop in system supply line. Limit controls (optional or supplied by others) such as supervisory relays for over-current, ground fault, or phase  imbalance  (supplied by others) may be connected  into the limit con- trol circuit.

2.1.4 Water Level Controls

The boiler water level control will be a proportional type regulator which will adjust the position of a valve in the feed-water supply line to maintain  the flow of feed- water to match the rate of steam  generation.  If a single dedicated  suitable feed- water pump is used, the control valve could be replaced by a variable speed control on the feedwater pump motor.

2.1.5 Conductivity Control and Sample Cooler Assembly

Conductivity of the water being circulated to the boiler electrodes will be controlled by an indicating type conductivity controller which will have separately  adjustable high and low set points. On actuation of the “high” set point, automatic  boiler bleed (surface blow- down) will begin and a light will indicate that bleed is in process.

“Low conductivity” closes a PLC contact and may be used to signal a chemical feed pump to start. Chemical feed pump is optional or supplied by others. It is not fur- nished as part of this boiler.

A Sample Cooler assembly shall be supplied, including the sample cooler, connec- tions for the boiler water, connections  for the cooling water, valves, conductivity measuring  cell, and manual  sampling valve.

2.2 Boiler Trim	The boiler will be supplied with the following trim items:

2.2.1 Pressure Control Piping

Pressure  gauges will indicate steam  pressure  in the boiler shell and in the user's steam header.  Gauge ranges shall be approximately 2 times the operating pressure. The Gauges and Pressure Controllers will be mounted on the boiler at eye level, pre- piped and pre-wired.

2.2.2 Water gauge glass

Water gauge glass complete with drain valve will be provided.

2.2.3 Water Column

A water column will be provided and will be suitable for mounting of the water gauge glass, gauge cocks, the water level controller and the high and low water cut- offs. A water column drain valve will be provided. A separate  control is provided for

the “Low-Low” water level protection.

2.2.4 Feed-water Valves

Boiler feed-water line will be equipped  with shut off valve and check valve between the boiler and the feed-water regulating valve or pump

2.2.5 Blow-down Valves

Boiler blow-off line will be fitted with one quick and one slow opening valve. Valves shall be “Y” pattern rated for boiler blow-off service.

2.2.6 Steam Valve

Boiler steam  outlet valves, such as a stop and check, are optional.

2.2.7 Back Pressure Regulating Valve

A pneumatic  back pressure regulating valve will be provided and will be adjusted  to throttle or close when the boiler steam  pressure drops below the operating pressure range. Valve and controller will be pneumatic  type. This Valve will protect the boiler against a sudden drop in system pressure.  Timing shall be adjusted for quick closing and slow opening.

2.2.8 Safety Valves

The boiler will have a minimum of two safety valves which shall be ASME rated and stamped. Aggregate capacity of the safety valves at their set pressure will not be less than 110% of the boiler rating in kilograms of steam  per hour. Boiler rated output will be taken as 3.5lbs  of steam  per KW. (1.59 kg of steam  per KW).

2.2.9 Bleed Valves (for conductivity control)

The boiler bleed (surface blow-down) valve shall be a needle type valve with cali- brated stem, optional adder for boiler. This valve shall be set to control the bleed rate. On-Off control of the bleed will be by means  of a separate  valve, air operated.

2.3 Insulation and

Casing

The boiler will be insulated  with 2” of glass fiber insulation secured to the boiler to prevent sagging. Insulation rings are provided on the boiler pressure  vessel. Insula- tion is covered by 18GA Aluminum sheets.

2.4 Top Cage	The boiler high voltage terminals will be enclosed in a preferably full height heavy screen enclosure with Kirk key interlock on access  opening to prevent entrance unless the boiler supply switch-gear is open. Kirk interlock shall be supplied by oth- ers. Switch-gear and Kirk key interlock provided by others

2.5 Control Panel	Power required to Control Panel is     _V, 3Ph,  	_Hz, incorporating a  	A

disconnect  switch.

All electrical controls, relays, pump and shield drive starters  and associated  push buttons,  lights, ammeters, and other components  of the boiler control system will be attached to

the boiler before shipment  and pre-wired with a 2 door NEMA 12 dust proof panel.

Power and Control sections are separate, each with front access.

The H.V. switch-gear (by others) should include CTs and PTs to be connected  (by others) to the Control Panel. In addition to their use for the boiler control logic, the information on V, A, KW is available in the PLC. KW value can be sent to a building system if desired.

3.0 Boiler Assembly and installation

The boiler will be shipped in two containers  or on a flat bed truck in main sections, and will require field erection and assembly and completion of electrical and piping connections.  The boiler manufacturer's  representative  will supply labor for the assembly and start-up  of the boiler. The representatives  will reassemble under supervision the internal components  of the boiler which were disassembled (Power Rods, Insulators and Boxes) before shipping in order to protect them in transit. Con- tainers should be opened at the site. This is an opportunity to train local personnel. Boiler access  is through the lower level manhole.

Insulated boiler is provided with lifting lugs for handling vertically or horizontally. Labor, material and equipment  required for setting of the boiler and electrical and piping work is not included in this proposal.

4.0Electrical Supply

System

4.1 High Voltage

Switchgear

The boiler will require a 3 phase,  4 wire supply circuit derived from a distribution or a transformer with a wye-connected  secondary and having the transformer neutral grounded at the transformer and extended by means of a full size insulated conduc- tor to the boiler neutral lug. The boiler shell and casing must also be grounded to the building ground system.  The motors specified for the boiler circulating pump and shield control and stand-by heater  will be  	V, 3Ph,  	Hz., unless oth- erwise specified. The boiler control circuits will be 120V, 1 phase,  	Hz.

High voltage switchgear for the boiler supply circuit is not included as a part of the boiler proposal. The boiler supply circuit switchgear shall be air or vacuum or SF6 circuit breaker rated for the boiler voltage and ampere load and should be equipped with protective relays as required to open the switchgear in event of phase  unbal- ance or loss of a phase,  over-current and under-voltage, and ground current.

The switchgear may also be such that it can be made to open by the boiler high pressure limit control for safety shutdown.  Instrumentation should include an ammeter  and an ammeter  switch for monitoring of phase  amperages. The breaker shall be equipped  with a Kirk key interlock which shall be keyed to match the access  door of the boiler high voltage terminal compartment described in par. 2.4.

It will be the Purchaser's  responsibility to advise the supplier of the switchgear of the need to coordinate the keying system with Cleaver-Brooks. Provide CT's and PT's for connection to boiler control circuit in boiler panel (2.5).  The switchgear shall incorporate a disconnect switch or equivalent means to provide a visible break in the power supply circuit to the boiler.

5.0 Feedwater

Treatment

No feed-water treatment  equipment  is included in this proposal. The necessary feed- water treatment  is not detailed in this typical specification.

The water hardness, required conductivity in the boiler shell, water pH, and alkalin-

ity play a key role in the proper functioning of the boiler. See Electrode Boilers

Required Water Quality Parameters table.

Boiler will operate at up to 3500 µmho conductivity for reduced blow-down and

750PPM alkalinity with superior insulators.