Section A10
Model CBR Steam Boiler

125-800 hp, Steam (15, 150, 200, or 250 psig) Sample Specification

# STEAM SPECIFICATIONS

Contents

PART 1 	GENERAL	A10-2

1.01	BOILER CHARACTERISTICS (STEAM)	A10-2

PART 2 	PRODUCTS	A10-2

2.01	GENERAL BOILER DESIGN	A10-2

2.02	BOILER SHELL (STEAM)	A10-2

2.03	STEAM BOILER TRIM	A10-3

2.04	BURNER	A10-4

2.05	EFFICIENCY GUARANTEE	A10-9

2.06	WARRANTY	A10-9

PART 3 	EXECUTION	A10-9

Model CBR Steam Boiler
(125-800 hp, Steam 15, 150, 200, or 250 psig)

The following sample specifications are provided by Cleaver-Brooks to assist you in specifying your customer's specific needs and application.

The Sample Specifications are typically utilized as the base template for the complete boiler specification. Contact your local Cleaver-Brooks authorized representative for information on special insurance requirements, special code requirements, optional equipment, or general assistance in completing the specification.

PART 1 	GENERAL

1.01	BOILER CHARACTERISTICS (STEAM)

A.	The Steam Boiler shall be Cleaver-Brooks Model CBR Fuel Series _____ (100,200, 700), _____ hp designed for _____ psig (15 or _____ psig steam). The maximum operating pressure shall be _____ psig.

B. 	The boiler shall have a maximum output of _____ Btu/hr, or _____horsepower when fired with CS12-48 No. 2 oil and/or natural gas, _____ Btu/cu-ft. Electrical power available shall be _____ Volt _____ Phase _____ Cycle and 115/1/60 for the control circuit.

PART 2 	PRODUCTS

2.01	GENERAL BOILER DESIGN

A.	The boiler shall be a two-pass horizontal firetube updraft boiler with _____ square feet of total heating surface for the _____ hp boiler. It shall be mounted on a heavy steel frame with integral forced draft burner and burner controls. The complete packaged boiler is built as a unit with Underwriters Laboratories listed controls.

The complete package boiler shall be approved as a unit by Underwriters Laboratories and shall bear the UL/cUL label, except in the case where 50 Hz has been selected.

1. 	The boiler shall be completely preassembled and fire tested at the factory. The unit shall be ready for immediate mounting on floor or simple foundation and ready for attachment of water, steam, fuel, electrical, vent, steam, and blowdown connections.

2.02	BOILER SHELL (STEAM)

1. 	The boiler shell must be constructed in accordance with ASME Boiler Code and must receive authorized boiler inspection prior to shipment. A copy of the inspection report shall be furnished the purchaser.

2. 	Two lifting eyes shall be located on top of the boiler.

3. 	Front and rear doors on the boiler shall be hinged or davited. Doors are to be sealed with fiberglass tadpole gaskets and fastened tightly using heavy capscrews that thread into replaceable brass nuts.

4. 	Rear refractory and insulation shall be contained in the formed door which must swing open for inspection of brick work.

5. 	The boiler tubes shall be rifled tube design, extending heat transfer surfaces.

6. 	Front and rear tube sheets and all tubes must be fully accessible for inspection and cleaning when the doors are swung open. The boiler shall be furnished with adequate handholes to facilitate boiler inspection and cleaning.

7. 	For boilers 125 horsepower and over, a manhole shall be provided.

8. 	The exhaust gas vent shall be located near the front of the boiler on the top center line and shall be capable of supporting:
125-225 hp 2000 lbs. and shall contain a stack thermometer.

9. 	Observation ports for the inspection of flame conditions shall be provided at each end of the boiler.

10. The boiler insulation shall consist of a 2 inch fiberglass blanket under a sectional preformed sheet metal lagging. This insulation must be readily removable and capable of being reinstalled, if required.

11. The entire boiler base frame and other components shall be factory painted before shipment using a hard-finish enamel coating.

2.03	STEAM BOILER TRIM

A. 	WATER COLUMN/LOW WATER CUTOFF AND WATER LEVEL CONTROL SYSTEM (150-250 psig design): Shall be a CB LEVEL MASTER Water level control system and shall be comprised of a microprocessor-based electronic controller, a non-contact, non-wearing, continuously reading absolute level sensor and pressure chamber. The control system shall be designed as follows: The electronic controller shall be panel mounted and operate in ambient temperatures from 32 degrees F to 125 degrees F, the pressure chamber shall be boiler mounted and operate to pressures of 250PSIG and the level sensor shall operate to pressures of 250 PSIG and temperatures to 400 degrees F. The pressure containing components shall be constructed in accordance with ASME Code. A shielded, four conductor cable with ground shall be run in metal conduit between the level sensor and the controller. Supply power shall be 115VAC-1 phase-60 Hz. All wiring shall be in compliance with the National ElectricalCode.

The pressure chamber shall have a sight glass mounted on the side. The level sensor shall have an accuracy of .01" or greater. The electronic controller shall have level and error indicating lights, alphanumeric display for messaging, reset/menu switch and the following features:

1. 	Continuous Level Indication

2.	Low Water Cutoff & Alarm

3. 	High Water Alarm

4. 	Low & High Water Warning

5. 	Full Modulating Control of Modulating Feedwater Control Valve

6.	Continuous Monitoring of Float Operation

7. 	Column Blowdown Detection and Reminder

8.	Auto or Manual Reset

9. 	Real Time Clock

10. 	Alarm Annunciation

11. 	Alarm History Files with Time Stamp

12. 	 Water Column Blowdown Record

13.	Auxiliary Low Water Cutoff Check

14.	 RS 232 Interface

15. 	Maximum Contacts Rating 15 amps Resistive Load

B. 	Feedwater Pump Control

The boiler feedwater pump control shall be included as an integral part of the water column to automatically actuate a motor driven feedwater pump maintaining the boiler water level within normal limits.

C.	Low Water Cutoff

The low water cutoff shall be included as an integral part of the boiler feedwater control wired into the burner control circuit to prevent burner operation if the boiler water level falls below a safe level.

D.	Auxiliary Low Water Cutoff

Auxiliary low water cutoff shall be included, piped to the vessel, and wired to the burner control circuit. A manual reset device shall be used on this control.

E. 	Steam Pressure Gauge

The steam pressure gauge shall be located at the front of the boiler and include cock and test connection.

F. 	Safety Relief Valves

Safety valves of a type and size to comply with ASME Code requirements shall be shipped loose.

G.	Steam Pressure Controls

The steam pressure control to regulate burner operation shall be mounted near the water column.

2.04	BURNER

A.	Mode of Operation

Burner operation shall be full modulation principle. The burner shall always return to low fire position for ignition.

B. 	Forced Draft Blower

1. 	All air for combustion shall be supplied by a forced draft blower mounted in the front boiler door, above the burner, to eliminate vibration and reduce noise level.

2.	Maximum sound level of the boiler/burner package shall not exceed _____ dBA (when measured in accordance with ABMA Sound Test Standards).

3. 	The impeller shall be cast aluminum, radial blade, carefully balanced, and directly connected to the blower motor shaft.

C.	Combustion Air Control

Combustion air damper and cam operated fuel metering valves shall be operated by a single damper control motor that regulates the fire according to load demand. Single point positioning controls shall be provided to regulate operation of the damper control motor.

D.	Fuel Specification and Piping

Refer to the following fuel series specifications:

•	Fuel series 700 - gas fired.

•	Fuel series 100 - light oil fired.

•	Fuel series 200 - light oil or gas fired.

Series 400 (heavy oil and gas) and series 600 (heavy oil only) also available. Check with your local Cleaver-Brooks representative for specification details.

1. 	Fuel Series 700 - Gas Fired

a.	Burner Type - The burner shall be integral with the front head of the boiler and of high radiant annular gas entry on 125-225 hp. and of high radiant multi-port type for gas burner 300-800 hp. The burner shall be approved for operation on natural gas fuel.

b.	Gas Pilot - The gas pilot shall be a premix type with automatic electric ignition. An electronic detector shall monitor the pilot so that the primary gas valve cannot open until pilot flame has been established. The pilot train shall include two manual shut-off valves, solenoid valve, pressure regulator and pressure gauge.

c.	Gas Burner Piping - Gas burner piping on all units shall include pressure regulating gas shutoff valve, motor operated with proof of closure switch and plugged leakage test connection. The valve is spring return to start or stop the gas burner and to close automatically in the event of power failure, flame failure, low water or any safety shutdown condition. A lubricating plug cock or butterfly shutoff valve shall be provided as a means for a tightness check of the primary shut off valve. An additional plug cock or butterfly shutoff valve shall be furnished at entrance to gas train. Select one of the following:

1) 	125-250 hp. High and low gas pressure switches shall be provided. A second motorized safety shutoff valve, plus an additional plugged leakage test connection shall be provided.

2) 	300-800 hp. High and low gas pressure switches shall be provided. A second motorized safety shutoff valve, plus an additional plugged leakage test connection shall be provided. A valve proving switch shall be located between the safety shutoff valves.

d.	Burner Turndown - Turndown range of the burner shall be 4:1 when firing natural gas.

1) 	125-200 hp. Turndown range of burner shall be 4:1 when firing natural gas.

2) 	250-800 hp. Turndown range of the burner shall be 10:1 when firing natural gas with a 60 or 30 ppm LE option.

2. 	Fuel Series 100 - Light Oil Fired

a.	Burner Type - The burner shall be integral with the front head of the boiler, and shall be a low pressure air atomizing type approved for operation with CS12-48, Commercial No. 2 oil.

b. 	Gas Pilot - The gas pilot shall be premix type with automatic electric ignition. An electronic detector shall monitor the pilot so that the primary fuel valve cannot open until flame has been established. The pilot train shall include two manual shut-off valves, solenoid valve, pressure regulator and pressure gauge.

c. 	Oil Pump - An oil pump with a capacity of approximately twice the maximum burning rate shall be included. A separate motor driven pump set, shipped loose to be installed in a location favorable to the oil storage tank, shall be provided.

d. 	Oil Burner Piping - Fuel oil piping on the unit shall include oil pressure regulating devices, oil metering controls, solenoid shutoff valves, pressure gauges and fuel strainer, all integrally mounted on the unit. A fuel oil controller shall be provided to combine all of the fuel oil controls into a single casting which is mounted on the front door of the unit. A single tip retractable nozzle shall be used for the low pressure air atomizing burner. A low oil pressure switch shall be included in the oil piping.

e. 	Low Pressure Air Atomizing - Select one of the following:

1) 	125-250 hp. High and low gas pressure switches shall be provided. A second motorized safety shutoff valve, plus an additional plugged leakage test connection shall be provided.

2) 	300-800 hp. High and low gas pressure switches shall be provided. A second motorized safety shutoff valve, plus an additional plugged leakage test connection shall be provided. A vent valve shall be located between the safety shutoff valves.

f. 	Burner Turndown - Select one of the following:

1) 	125-200 hp. Turndown range of burner shall be 4:1 when firing natural gas.

2) 	250-800 hp. Turndown range of the burner shall be 10:1 when firing natural gas with a 60 or 30 ppm LE option.

3. 	Fuel series 200 - Light Oil or Gas Fired

a. 	Burner Type - The burner, integral with the front head of the boiler, shall be a combination of the low pressure air atomizing type for oil and high radiant annular gas entry on 125-225 hp and multi-port type for gas entry on 100 hp. The burner shall be approved for operation with either CS12-48 Commercial No. 2 Oil or natural gas.

b. 	Gas Pilot - The gas pilot shall be premix type with automatic electric ignition. An electronic detector shall monitor the pilot so that the primary fuel valve cannot open until flame has been established. The pilot train shall include two manual shut-off valves, solenoid valve, pressure regulator and pressure gauge.

c. 	Oil Burner

Oil Pump - An oil pump with a capacity of approximately twice the maximum burning rate shall be included. A separate motor driven pump set, shipped loose, to be installed in a location favorable to the oil storage tank, shall be provided.

Oil Burner Piping - Fuel oil piping on the unit shall include oil pressure regulating devices, oil metering controls, solenoid shutoff valves, pressure gauges and fuel strainer, all integrally mounted on the unit. A fuel oil controller shall be provided to combine all of the fuel oil controls into a single casting which is mounted on the front door of the unit. A single tip retractable nozzle shall be used for the low pressure air atomizing burner. A low oil pressure switch shall be included in the oil piping.

Low pressure air atomizing - Separate air compressor module mounted on boiler base rail with low atomizing air pressure switch.

d. 	Gas Burner

1) 	Gas Burner Piping - gas burner piping on all units shall include pressure regulating gas shutoff valve, motor operated with proof of closure switch and plugged leakage test connection. The valve is spring return to start or stop the gas burner and to close automatically in the event of power failure, flame failure, low water or any safety shutdown condition. A lubricating plug cock or butterfly shutoff valve shall be provided as a means for a tightness check of the primary shut off valve. An additional plug cock or butterfly shutoff valve shall be furnished at entrance to gas train. Select one of the following:

•	125-250 hp. High and low gas pressure switches shall be provided. A second motorized safety shutoff valve, plus an additional plugged leakage test connection shall be provided.

•	300-800 hp. High and low gas pressure switches shall be provided. A second motorized safety shutoff valve, plus and additional plugged leakage test connection shall be provided. A valve proving switch shall be located between the safety shutoff valves.

e. 	Burner Turndown - Select one of the following:

•	125-200 hp. Turndown range of the burner shall be 4:1.

•	250-800 hp. Turndown range of the burner shall be 10:1 when firing natural gas and 8:1 on No. 2 oil.

E. 	Boiler Flame Safeguard Controller and Control Panel

1. 	CB780E Flame Safeguard Controller

Each boiler shall be factory equipped with flame safeguard controller providing technology and functions equal to the Cleaver-Brooks Model CB780E.

Controller shall be computerized solid state having sequence and flame-on lights and digital “first out” fault code indications of flame safeguard trip functions. It shall include dynamic self-check logic. The controller shall have a fixed operating sequence incapable of being manually altered. The sequence shall include start, pre-purge, pilot and main fuel ignition run and post-purge cycles.

Controller shall be the non-recycle type for maximum safety that shall shutdown the burner and indicate as a minimum the following trip functions: pilot and main flame failure, high and low fire proving switch faults, running interlocks open, false flame signal and fuel valve open (when proof of closure switch is furnished).

The controller shall have a run/test switch. It shall allow interruptions to sequence just after pre-purge, during pilot ignition trial and run cycles for adjustments to firing rate motor, damper linkages and pilot flame for minimum turndown tests.

a. 	Control Panel - The control panel shall be mounted on the front door of the boiler in a location convenient to the operator. The hinged metal cabinet will have NEMA 1A rating that includes a neoprene dust seal and a Yale cabinet key type lock.

The panel shall contain the boiler flame safeguard controller, blower motor starter, indicating lights and selector switches.

The panel shall have a removable sub-base for mounting the flame safeguard controller, blower motor starter, and terminal blocks. For combination gas-oil fired boilers, the panel shall contain the fuel selector switch.

b. 	Lights

•	White - load demand.

•	White - fuel valve open.

•	Red - low water.

•	Red - flame failure.

c.	Control Switches

•	Burner On-Off.

•	Manual-Automatic.

•	Manual Firing Rate Control.

d. 	Oil, heat and moisture resistant wire shall be used and identified with circuit numbers corresponding to the electrical wiring diagram.

e. 	All electrical equipment and wiring shall be in conformance with Underwriters Laboratories requirements.

f. 	Boiler to be supplied with a control circuit transformer and fuse protection for the control circuit.

2. 	Control Panel

a. 	The control panel shall be mounted on the front door of the boiler in a location convenient to the operator. The hinged metal cabinet will have NEMA 1A rating that includes a neoprene dust seal and a Yale cabinet key type lock.

b. 	The panel shall contain the boiler flame safeguard controller, blower motor starter, indicating lights and selector switches.

c. 	Panel shall have a removable sub-base for mounting the flame safeguard controller, blower motor starter, and terminal blocks. For combination gas-oil fired boilers the panel shall contain the fuel selector switch.

d. 	Oil, heat, and moisture resistant wire shall be used and identified with circuit numbers corresponding to the electrical wiring diagram.

e. 	All electrical equipment and wiring shall be in conformance with Underwriters Laboratories requirements.

f. 	Boiler to be supplied with a control circuit transformer and fuse protection for the control circuit.

2.05	EFFICIENCY GUARANTEE

The boiler must be guaranteed to operate at a minimum fuel-to-steam efficiency of 	 percent from 25 to 100 percent of rating when burning natural gas and 	fuel-to- steam efficiency at 100% firing rate when burning oil.

The specified boiler efficiency is based on the following conditions.

A. 	Fuel specification used to determine boiler efficiency:

• 	Natural Gas
Carbon, % (wt) = 69.98
Hydrogen, % (wt) = 22.31
Sulfur, % (wt) = 0.0
Heating value, Btu/lb = 21,830

• 	No. 2 Oil
Carbon, % (wt) = 85.8
Hydrogen, % (wt) = 12.7
Sulfur, % (wt) = 0.2
Heating value, Btu/lb = 19,420

• No. 6 Oil
Carbon, % (wt) = 86.6
Hydrogen, % (wt) = 10.9
Sulfur, % (wt) = 2.09
Heating value, Btu/lb = 18,830

2.06	WARRANTY

A.	All equipment is to be guaranteed against defects in materials and/or workmanship for a period of 12 months from date of start-up or 18 months from date of shipment, whichever comes first.

PART 3 	EXECUTION

A.	Shop Tests

The packaged boiler must receive factory tests to check the construction, controls, and operation of the unit. All tests may be witnessed by the purchaser, if desired.

B. 	Start-up Service

1. 	After boiler installation is completed, the manufacturer shall provide the services of a field representative for starting the unit and timing the operator at no additional costs.

a. 	A factory approved and authorized start-up report shall be submitted to the customer/user at the time of start-up.